## Data Center
Date
Data Center Technical Data Request (based on NERC Questionnaire, https://www.nerc.com/comm/RSTC/LMWG/Data%20Center%20Information%20Collection%20Questionnaire.pdf) 03/31/2026
1 | What is the data center type?
|  | a. Cloud | Choose
|  | b. Artificial Intelligence (AI) training | Choose
|  | c. Cryptocurrency | Choose
d. Other (please specify)
2 | What is the rated total MW consumption an power factor of your data center, including IT equipment, power distribution, and cooling?
|  | Total MW : |  | Power factor*:
3 | What is the percentage of the following load components of the total MW consumption of the data center?
computing/server load:
lighting load:
power distribution losses:
cooling:
|  | other: |  | please describe if "other" is applicable:
Does the percentage change during different seasons and different times of the day? If yes, a gross estimate like Summer Day/ Summer Night and Winter Day/Winter Night would help.
4 | If the data center has some form of forced cooling system, what is this comprised of?
|  | a. Computer Room Air Conditioners (CRACs) with internal compressors |  |  | Choose | add details if needed
|  | b. Computer Room Air Handlers (CRAHs) supplied with chilled water. |  |  | Choose | add details if needed
|  | c. Air-Handling Units (AHUs) dedicated to the data center space |  |  | Choose | add details if needed
|  | d. Other (please describe) |  |  | Choose | add details if needed
5 | Are the motor-driven components of the cooling systems driven by:
|  | a. Single-speed motors that are operated across the line (Motors connected directly to the AC supply) |  |  | Choose | add details if needed
|  | b. Motors controlled by variable/adjustable speed drives or electronically commutated motors (ECMs) |  |  | Choose | add details if needed
|  | c. Other methods (please specify) |  |  | Choose | add details if needed
6 | At what voltage sag levels and durations below which, the components within the data center disconnect from the grid?
a. Voltage sag level(s)/duration(s) at which the computer/server load disconnects from the utility system (these may transfer to a local UPS)?
b. Voltage sag level(s)/duration(s) at which the cooling load disconnects from the system (these may transfer to an emergency generator or local power source)?
c. Are the voltage sags measured on a per phase basis for the disconnection action or are these measured as rms considering the 3 phases?
d. Will any part of the load disconnect from the grid after certain number of voltage sag events in a specific period of time? If yes, what are the sag threshold and duration for the specific period?
e. Any other protection scheme related to voltage sag which may disconnect any load from the grid?
7 | At what voltage swell levels and durations above which, the components within the data center disconnect from the grid?
a. Voltage sag level(s)/duration(s) at which the computer/server load disconnects from the utility system (these may transfer to a local UPS)?
b. Voltage sag level(s)/duration(s) at which the cooling load disconnects from the system (these may transfer to an emergency generator or local power source)?
c. Are the voltage sags measured on a per phase basis for the disconnection action or are these measured as rms considering the 3 phases?
d. Will any part of the load disconnect from the grid after certain number of voltage sag events in a specific period of time? If yes, what are the sag threshold and duration for the specific period?
e. Any other protection scheme related to voltage sag which may disconnect any load from the grid?
8 | Are there any frequency thresholds below and above which the data center computer/server load may disconnect from the system?
9 | If the loads disconnect from the utility grid, how do they reconnect back when the voltage and frequency returns to normal values?
a. Do they reconnect immediately when the voltage and frequency recovers to certain levels. Please specify the voltage and frequency levels.
b. Do they reconnect with a delay when the voltage and frequency recovers to certain levels. Please specify the voltage and frequency levels and delays.
c. Do you reconnect manually?
d. Do they reconnect with a ramp as or after voltage and frequency recovers to a certain level, please specify the voltage and frequency levels and ramp rate at which these loads get reconnected back (if it’s in steps please approximately provide information on how that happens).
10 | Is there a backup system to supply the data center in the event of disconnection from the grid?
a. What is the size of the data center Emergency Generator (EG) and Battery Energy Storage (BESS) in relation to the data center load
b. Can the EG and BESS be dispatched to support the entire/partial load during system events? If so, for how many hours?
c. Can the Data center be Islanded with only the EG and BESS in event of a planned or unplanned disconnection from grid?
d. Can the Data Center participate on demand side management in a grid emergency or as an ancillary service?
e. How much of the server farm load could be picked up by or redistributed to redundant server sites across the world?
f. In the event of a data center being tripped offline, how much of that load would they transfer somewhere else?
g. How fast can this load transfer be done?
h. Is it closed transition (Make Before Break) or open transition (Break Before Make)?
11 | Would the Data Center have onsite generation (such as solar, fuel cell) and/or energy storage facilities to serve the demand when available? If yes:
Please provide the generation and energy storage capacity.
a. Would they normally parallel with the electrical grid?
b. Would they export to the grid?
12 | Provide SLD showing point of interconnection requested
13 | Provide details of Existing protection / control scheme that impacts the response of data center load to voltage disturbances or frequency disturbances.
14 | What is the duration of outage (in seconds or minutes) that will be acceptable to you.
15 | Please provide any additional information about the data center project .
* : See ISO Tariff for load power factor requirements

## dyd models
Notes: |  |  | customer input required
Please fill in the highlighted fields with data.
Customers are encouraged to refer to the PSLF User Manual and available documentation from NERC on use and parameterization of model parameters
For fields, if not applicable (example-DG data), please fill in as "N/A"
If multiple motors or Type 1 loads need to be represented, please copy and paste relevant fields and identify applicable parameters( for example - LFm1, LFm2, Rsn1, Rsn2)
Model Name | Description | PSLF Variable
CMPLDW
Composite Load Model (cmpldw) | Substation shunt capacitor susceptance, p.u. | Bss
Composite Load Model (cmpldw) | Feeder equivalent resistance, p.u. | Rfdr
Composite Load Model (cmpldw) | Feeder equivalent reactance, p.u. | Xfdr
Composite Load Model (cmpldw) | Fraction of feeder shunt capacitance at substation bus end | Fb
Composite Load Model (cmpldw) | Substation transformer reactance, p.u. | Xxf
Composite Load Model (cmpldw) | Transformer high side fixed tap, p.u. | Tfixhs
Composite Load Model (cmpldw) | Transformer low side fixed tap, p.u. | Tfixls
Composite Load Model (cmpldw) | 1 for automatic tap adjustment (low side variable tap) | LTC
Composite Load Model (cmpldw) | Minimum variable tap, p.u. | Tmin
Composite Load Model (cmpldw) | Maximum variable tap, p.u. | Tmax
Composite Load Model (cmpldw) | Variable tap step size, p.u. | step
Composite Load Model (cmpldw) | Minimum low-side voltage, p.u. | Vmin
Composite Load Model (cmpldw) | Maximum low-side voltage, p.u. | Vmax
Composite Load Model (cmpldw) | Time delay to initiate tap adjustment, sec. | Tdel
Composite Load Model (cmpldw) | Time delay between tap steps, sec. | Ttap
Composite Load Model (cmpldw) | Transformer LTC compensating resistance, p.u. | Rcmp
Composite Load Model (cmpldw) | Transformer LTC compensating reactance, p.u. | Xcmp
Composite Load Model (cmpldw) | Motor A fraction of load P | FmA
Composite Load Model (cmpldw) | Motor B fraction of load P | FmB
Composite Load Model (cmpldw) | Motor C fraction of load P | FmC
Composite Load Model (cmpldw) | Motor D fraction of load P | FmD
Composite Load Model (cmpldw) | Electronic load fraction of load P | Fel
Composite Load Model (cmpldw) | Electronic load power factor | PFel
Composite Load Model (cmpldw) | Voltage below which electronic load decreases, p.u. | Vd1
Composite Load Model (cmpldw) | Voltage below which electronic load is zero, p.u. | Vd2
Composite Load Model (cmpldw) | Fraction of electronic load that recovers from low voltage trip | frcel
Composite Load Model (cmpldw) | Power factor of static load component | PFs
Composite Load Model (cmpldw) | Static load - exponent of first P term | P1e
Composite Load Model (cmpldw) | Static load - coefficient of first P term | P1c
Composite Load Model (cmpldw) | Static load - exponent of second P term | P2e
Composite Load Model (cmpldw) | Static load - coefficient of second P term | P2c
Composite Load Model (cmpldw) | Frequency sensitivity factor for P | Pfrq
Composite Load Model (cmpldw) | Static load - exponent of first Q term | Q1e
Composite Load Model (cmpldw) | Static load - coefficient of first Q term | Q1c
Composite Load Model (cmpldw) | Static load - exponent of second Q term | Q2e
Composite Load Model (cmpldw) | Static load - coefficient of second Q term | Q2c
Composite Load Model (cmpldw) | Frequency sensitivity factor for Q | Qfrq
Composite Load Model (cmpldw) | First motor type | Mtypa
Composite Load Model (cmpldw) | Second motor type | Mtypb
Composite Load Model (cmpldw) | Third motor type | Mtypc
Composite Load Model (cmpldw) | Fourth Motor type | Mtypd
Composite Load Model (cmpldw) | For Type 3 motor, the following parameters must be input:
Composite Load Model (cmpldw) | Motor loading factor | LFmn
Composite Load Model (cmpldw) | Stator resistance, p.u. | Rsn
Composite Load Model (cmpldw) | Synchronous reactance, p.u. | Lsn
Composite Load Model (cmpldw) | Transient reactance, p.u. | Lpn
Composite Load Model (cmpldw) | Subtransient reactance, p.u. | Lppn
Composite Load Model (cmpldw) | Transient open circuit time constant, sec. | Tpon
Composite Load Model (cmpldw) | Subtransient open circuit time constant, sec. | Tppon
Composite Load Model (cmpldw) | Inertia constant, sec. | Hn
Composite Load Model (cmpldw) | Mechanical torque exponent | Etrqn
Composite Load Model (cmpldw) | First low voltage trip level, p.u. V | Vtr1n
Composite Load Model (cmpldw) | First low voltage trip delay time, sec. | Ttr1n
Composite Load Model (cmpldw) | First low voltage trip fraction | Ftr1n
Composite Load Model (cmpldw) | First low voltage reconnection level, p.u. V | Vrc1n
Composite Load Model (cmpldw) | First low voltage reconnection delay time, sec. | Trc1n
Composite Load Model (cmpldw) | Second low voltage trip level, p.u. V | Vtr2n
Composite Load Model (cmpldw) | Second low voltage trip delay time, sec. | Ttr2n
Composite Load Model (cmpldw) | Second low voltage trip fraction | Ftr2n
Composite Load Model (cmpldw) | Second low voltage reconnection level, p.u. V | Vrc2n
Composite Load Model (cmpldw) | Second low voltage reconnection delay time, sec. | Trc2n
Composite Load Model (cmpldw) | For Type 1 A/C load, the following parameters must be input:
Composite Load Model (cmpldw) | Motor loading factor (Type 1 A/C) | LFmn
Composite Load Model (cmpldw) | Power factor | CompPFn
Composite Load Model (cmpldw) | Stall voltage, p.u. | Vstalln
Composite Load Model (cmpldw) | Stall resistance, p.u. | Rstalln
Composite Load Model (cmpldw) | Stall reactance, p.u. | Xstalln
Composite Load Model (cmpldw) | Stall time delay, sec. | Tstalln
Composite Load Model (cmpldw) | Fraction of load that can restart after stalling | Frstn
Composite Load Model (cmpldw) | Voltage at which restart can occur, p.u. | Vrstn
Composite Load Model (cmpldw) | Restart time delay, sec. | Trstn
Composite Load Model (cmpldw) | Fraction of load with undervoltage relay protection | Fuvrn
Composite Load Model (cmpldw) | First undervoltage trip level, p.u. | Vtr1n
Composite Load Model (cmpldw) | First undervoltage trip delay time, sec. | Ttr1n
Composite Load Model (cmpldw) | Second undervoltage trip level, p.u. | Vtr2n
Composite Load Model (cmpldw) | Second undervoltage trip delay time, sec. | Ttr2n
Composite Load Model (cmpldw) | Contactor voltage at which tripping starts, p.u. | Vc1offn
Composite Load Model (cmpldw) | Contactor voltage at which tripping is complete p.u. | Vc2offn
Composite Load Model (cmpldw) | Contactor voltage at which reconnection is complete, p.u. | Vc1onn
Composite Load Model (cmpldw) | Contactor voltage at which reconnection starts, p.u. | Vc2onn
Composite Load Model (cmpldw) | Thermal time constant, sec. | Tthn
Composite Load Model (cmpldw) | Thermal protection trip start level, p.u. temperature | Th1tn
Composite Load Model (cmpldw) | Thermal protection trip completion level, p.u. temperature | Th2tn
Composite Load Model (cmpldw) | Voltage measurement lag, sec. | Tvn
Composite Load Model (cmpldw) | For simplified photovoltaic DG model (DGPV), the following parameters must be input:
Composite Load Model (cmpldw) | 1 - DGPV; 0 - none; 2 - der_a | DGtype
Composite Load Model (cmpldw) | Initial Pdg method | Pflgdg
Composite Load Model (cmpldw) | DG fraction or MW | Pgdg
Composite Load Model (cmpldw) | DG power factor (for Pflgdg = 0 or 1) | PFdg
Composite Load Model (cmpldw) | Current limit, p.u. | Imax
Composite Load Model (cmpldw) | Voltage below which all DG is tripped, p.u. | Vt0
Composite Load Model (cmpldw) | Voltage below which DG starts to be tripped, p.u. | Vt1
Composite Load Model (cmpldw) | Voltage above which DG starts to be tripped, p.u. | Vt2
Composite Load Model (cmpldw) | Voltage above which all DG is tripped, p.u. | Vt3
Composite Load Model (cmpldw) | Fraction of DG that restarts when voltage recovers | Vrec
Composite Load Model (cmpldw) | Frequency below which all DG is tripped, Hz. | Ft0
Composite Load Model (cmpldw) | Frequency below which DG starts to be tripped, Hz. | Ft1
Composite Load Model (cmpldw) | Frequency above which DG starts to be tripped, Hz. | Ft2
Composite Load Model (cmpldw) | Frequency above which all DG is tripped, Hz. | Ft3
Composite Load Model (cmpldw) | Fraction of DG that restarts when frequency recovers | Frec
Composite Load Model (cmpldw) | Voltage measurement lag, sec. | Tvn
Composite Load Model (cmpldw) | For Detailed DG model
Composite Load Model (cmpldw) | 2 - der_a; 0 - none; 1 - DGPV | DGtype
Composite Load Model (cmpldw) | Data ID number for _cmp_der_a data mgmt. model | DGdatno
Composite Load Model (cmpldw) | MVA base of DG; if negative abs. value is a loading factor | DGmbase
CMP_EV1
EV Model (cmp_ev1) | Loading factor | lfm
EV Model (cmp_ev1) | Voltage measurement time constant (s) | tfltr
EV Model (cmp_ev1) | Deadband on frequency response, pu | dbd
EV Model (cmp_ev1) | Frequency droop gain | kdroop
EV Model (cmp_ev1) | Active power washout (Proportional constant) | kvp
EV Model (cmp_ev1) | Active power washout (Time constant) (s) | tvp
EV Model (cmp_ev1) | Q/P ratio for Q0 computation from P0 | qp
EV Model (cmp_ev1) | Reactive power washout (Proportional constant) | kvq
EV Model (cmp_ev1) | Reactive power washout (Time constant) (s) | tvq
EV Model (cmp_ev1) | Lead time constant (s) | ta
EV Model (cmp_ev1) | Lag time constant (s) | tb
EV Model (cmp_ev1) | Fraction of Type A Evs | frA
EV Model (cmp_ev1) | Fraction of Type B Evs | frB
EV Model (cmp_ev1) | Fraction of Type C Evs | frC
EV Model (cmp_ev1) | Active Power Exponential (FrA) | nPA
EV Model (cmp_ev1) | Reactive Power Exponential (FrA) | nQA
EV Model (cmp_ev1) | Active Power Exponential (FrB) | nPB
EV Model (cmp_ev1) | Reactive Power Exponential (FrB) | nQB
EV Model (cmp_ev1) | Active Power Exponential (FrC) | nPC
EV Model (cmp_ev1) | Reactive Power Exponential (FrC) | nQC
EV Model (cmp_ev1) | Active Power Exponential (FrD) | nPD
EV Model (cmp_ev1) | Reactive Power Exponential (FrD) | nQD
EV Model (cmp_ev1) | fraction of EV that will cease (FrA) | fcA
EV Model (cmp_ev1) | Voltage threshold for cease logic (FrA) (pu) | vcA
EV Model (cmp_ev1) | Time delay for cease logic to be initiated (FrA) (s) | tcA
EV Model (cmp_ev1) | Time delay to cease after detection (FrA) (s) | tdelayA
EV Model (cmp_ev1) | Voltage threshold to initiate power ramp logic (FrA) (pu) | vrA
EV Model (cmp_ev1) | Time delay for ramp up logic to be initiated (FrA) (s) | trA
EV Model (cmp_ev1) | Ramp up time (FrA) (s) | trampA
EV Model (cmp_ev1) | fraction of EV that will cease (FrB) | fcB
EV Model (cmp_ev1) | Voltage threshold for cease logic (FrB) (pu) | vcB
EV Model (cmp_ev1) | Time delay for cease logic to be initiated (FrB) (s) | tcB
EV Model (cmp_ev1) | Time delay to cease after detection (FrB) (s) | tdelayB
EV Model (cmp_ev1) | Voltage threshold to initiate power ramp logic (FrB) (pu) | vrB
EV Model (cmp_ev1) | Time delay for ramp up logic to be initiated (FrB) (s) | trB
EV Model (cmp_ev1) | Ramp up time (FrB) (s) | trampB
EV Model (cmp_ev1) | fraction of EV that will cease (FrC) | fcC
EV Model (cmp_ev1) | Voltage threshold for cease logic (FrC) (pu) | vcC
EV Model (cmp_ev1) | Time delay for cease logic to be initiated (FrC) (s) | tcC
EV Model (cmp_ev1) | Time delay to cease after detection (FrC) (s) | tdelayC
EV Model (cmp_ev1) | Voltage threshold to initiate power ramp logic (FrC) (pu) | vrC
EV Model (cmp_ev1) | Time delay for ramp up logic to be initiated (FrC) (s) | trC
EV Model (cmp_ev1) | Ramp up time (FrC) (s) | trampC
EV Model (cmp_ev1) | maximum Ip (pu) | ipmax
EV Model (cmp_ev1) | minimum Ip (pu) | ipmin
EV Model (cmp_ev1) | maximum Iq (pu) | iqmax
EV Model (cmp_ev1) | minimum Iq (pu) | iqmin
EV Model (cmp_ev1) | Time step subdivision factor | ndelt
EV Model (cmp_ev1) | Time delay in charger controls | tnum
LSDT1
Frequency Relay (lsdt1) | First stage pick-up value, hz | F1
Frequency Relay (lsdt1) | First stage time delay, sec. | T1
Frequency Relay (lsdt1) | First stage breaker delay, sec. | Tcb1
Frequency Relay (lsdt1) | First stage shedding fraction, p.u. | sf1
Frequency Relay (lsdt1) | Second stage pick-up value, hz | F2
Frequency Relay (lsdt1) | Second stage time delay, sec. | T2
Frequency Relay (lsdt1) | Second stage breaker delay, sec. | Tcb2
Frequency Relay (lsdt1) | Second stage shedding fraction, p.u. | sf2
Frequency Relay (lsdt1) | Third stage pick-up value, p.u. | F3
Frequency Relay (lsdt1) | Third stage time delay, sec. | T3
Frequency Relay (lsdt1) | Third stage breaker delay, sec. | Tcb3
Frequency Relay (lsdt1) | Third stage shedding fraction, p.u. | sf3
Frequency Relay (lsdt1) | Reset time, sec. | Treset
Frequency Relay (lsdt1) | Input transducer time constant, sec. | Tfilter